## Slide 1: Interaction Analysis for Multi-Loop Control

## Slide 2: Multivariable Process Control
Industrial Processes
  multivariable (multiple inputs influence same output) and exhibit strong interaction among the variables
Conventional Control scheme
  Multiple Single Input Single Output PID controllers used for controlling plant (Multi-Loop Control)
Consequences
  Loop Interactions
  Lack of coordination between different PID loops
  Neighboring PID loops can co-operate with each other or end up opposing / disturbing each other

## Slide 3: Quadruple Tank

## Slide 4: Block Diagram : Quad Tank

## Slide 5: Loop Interactions : Quad Tank

## Slide 6: Shell Control Problem

## Slide 7: Shell Control Problem
Control Scheme 1
  PID-1: (y1) Top End Point - (u1) Top Draw
  PID-2: (y2) Side Endpoint - (u2) Side Draw
  PID-3: (y3) Bottom Reflux Temperature – (u3) Bottom Reflux Duty
Control Scheme 2
  PID-1: (y2) Side End Point - (u1) Top Draw
  PID-2: (y1) Top Endpoint - (u2) Side Draw
  PID-3: (y3) Bottom Reflux Temperature –(u3) Bottom Reflux Duty
How to examine above options systematically and reach a decision ?

## Slide 8: Tennesse Eastman Problem
Primary Controlled Variable: G conc in Product and Product flow rate

## Slide 9: Input - Output Variables

## Slide 10: Loop Interactions
Large loop interactions :
  can lead to poor quality of control due to lack of coordination among PID controllers
Solution strategy:
  Choose controller pairing with minimal interactions
  De-tune the controllers to minimize loop interactions
  Design multi-variable controllers, which simultaneously Change all inputs by considering errors in all the outputs

## Slide 11: Quadruple Tank process
LT
LT
LC
LC

## Slide 12: Block Diagram : Quad Tank

## Slide 13: Loop Interactions : Quad Tank

## Slide 14: Interaction Analysis
Assume a loop pairing say y1-u1 and perform the following experiments
With all loops open, make a step change in u1 to u1+ Δu and measure the change in output Δy1.
We will term this as a direct effect.
With all loops except the u1-y1 loop closed, repeat the same change in u1.
There will be change in y1 because of the direct effect but also there will be a retaliatory effect because u2 changes to keep y2 constant.
We will term this change as Δy1+Δy1r

## Slide 15: Interaction Analysis
Ratio of these two terms can be defined as λ11 (for the y1-u1 pairing) as
λ11 = Δy1/( Δy1+Δy1r)
This is called relative gain
Compute relative gain for each assumed input/output pairing
Depending on the values of this index for various assumed loop pairings (step 1), decision can be taken on the final loop pairing.
This decision making is based on steady state analysis only.

## Slide 16: Relative Gain Array (RGA)

## Slide 17: Calculation of RGA

## Slide 18: Calculation of RGA

## Slide 19: Calculation of RGA

## Slide 20: Wood-Berry Column

## Slide 21: Wood-Berry Column

## Slide 22: Wood-Berry Column
Multi-Loop PID Control
Change in closed loop behavior due to loop interactions

## Slide 23: RGA calculation for MIMO Process

## Slide 24: MIMO RGA Calculation

## Slide 25: RGA for Blending Tank
Process: Blending of two process streams to get desired composition of A in the product.
Control objective : m,x by manipulating m1 and m2
Desired value for m and x is m* and x*. Find RGA
m1, Pure A
m2, Pure B
m, x

## Slide 26: RGA for Blending Tank
Total Mass Balance :
Comp A balance:
will give
so,

## Slide 27: Analysis of RGA
and in same direction to
but direction of Kr is opposite to Kd

## Slide 28: Analysis of RGA
If λ11 =1 ⇒ retaliatory action is not present. So assumed loop pairing is correct because there is no interaction from the other loop.
If 0 < λ11 < 1 ⇒ retaliatory action is comparable to the direct action but is in the same direction. The assumed loop pairing may be chosen only if the index is closer to 1 (say 0.8).
If λ11 =0 ⇒ Retaliatory action is much greater than the direct action. The assumed loop pairing is incorrect. The loop pairing u1-y2 is preferable

## Slide 29: Analysis of RGA
If λ11 > 1 ⇒ Retaliatory action is in opposite direction to the direct action but is smaller in magnitude than the direct. The assumed loop pairing may be chosen only if the index is close to 1.
If λ11 < 0, Retaliatory effect is larger and opposite in direction to the main effect. Do not choose this loop pairing.

## Slide 30: Suggested Loop Pairing
Refinery Distillation Column

## Slide 31: RGA analysis : Non-square System

## Slide 32: Singular Value Analysis
Powerful analytical tool for
Selection of controlled, measured and manipulated variables
Determination of best multi-loop configuration
Evaluation of robustness (insensitivity to changes in plant behavior) of a control scheme

## Slide 33: Singular Value Analysis
Non-square systems (number of inputs not equal to number of outputs)
  SVA can be used to find a square subset with least difficulties in control
Larger condition number implies difficulties in controlling a system
  Among multiple possibilities, choose subset with minimum condition number
Limitation: Singular values are dependent on scaling of input and output variables

## Slide 34: Singular Value Decomposition
S is diagonal matrix of singular values (s1, s2, …, sr)
The singular values are the positive square roots of the eigenvalues of (r = rank of )
W,V are input and output singular vectors
Columns of W and V are orthonormal.
Calculate S, W, V using MATLAB (svd = singular value decomposition)
Condition number (CN) is the ratio of the largest to the smallest singular value and indicates if K is ill-conditioned.

## Slide 35: Singular Value Analysis
SVD of K :
Pairing rule:
Output associated with the largest magnitude element (without regard to sign) of the W1 vector with the manipulated variable associated with the largest magnitude element (without regard to sign) of the V1 vector. Same logic will apply for W2 – V2 … Wn – Vn vectors.
Alternate Method
Arrange the singular values in order of largest to smallest and look for any σi/σi-1 > 10; then one or more inputs (or outputs) can be deleted.
Delete one row and one column of K at a time and evaluate the properties of the reduced gain matrix.

## Slide 36: Example
RGA=

## Slide 37: Quadruple Tank Process
Schematic of Quadruple Tank Process

## Slide 38: Quadruple Tank problem
Control Objective
Both the levels of tank1 and tank2 should be controlled by manipulating voltages to the pumps.
Data for simulation:
A1, A3 = 28 cm2
A2, A4 = 32 cm2
a1, a3 = 0.071 cm2
a2, a4 = 0.057 cm2
Case | k1 | k2 | v1 | v2 |  | 
1 | 3.33 | 3.35 | 3.0 | 3.0 | 0.7 | 0.6
2 | 3.14 | 3.29 | 3.15 | 3.15 | 0.43 | 0.34
3 | 3.2 | 3.32 | 3.1 | 3.1 | 0.5 | 0.5
Case | k1 | k2 | v1 | v2 |  | 
1 | 3.33 | 3.35 | 3.0 | 3.0 | 0.7 | 0.6
2 | 3.14 | 3.29 | 3.15 | 3.15 | 0.43 | 0.34
3 | 3.2 | 3.32 | 3.1 | 3.1 | 0.5 | 0.5

## Slide 39: Block Diagram : Quad Tank

## Slide 40: Quad Tank : Case 1

## Slide 41: Quad Tank: Case 2

## Slide 42: Quad Tank: Case 3

## Slide 43: Quad Tank
Case 1
Case 2

## Slide 44: Quad Tank:

## Slide 45: Quad Tank
Case 3

## Slide 46: Furnace Control

## Slide 47: 4-Component Distillation Column

## Slide 48: Niederlinsky Index
Consider MIMO system whose inputs and outputs are paired as i.e, Transfer Function matrix G(s) is arranged such that transfer functions relating paired inputs and outputs are arranged along the diagonal.
Further, let each element of G(s) be (a) rational and (b) open loop stable.
Also, let n SISO feedback controllers with integral action be designed such that each SISO loop is stable when all the rest ( n-1) loops are open.
Under these assumptions, the multi-loop control system will be unstable for all possible values of controller parameters if the Niederlinsky Index (NI) defined as

## Slide 49: Furnace Control

## Slide 50: Multi-Loop PID Control
After selection of loop pairings with minimum interactions, one can design controllers for individual loops.
Presence of interaction and retaliatory effects from other loops may require that the controller be detuned for acceptable performance.
  BLT Detuning method
  Sequential Loop Tuning
  Independent Loop Tuning

## Slide 51
McAvoy method

## Slide 52: Biggest Log Modulus Tuning (BLT)
SISO Loop Design Review:
Characteristic Eqn.
Nyquist Plot: depicts real part of GOL(s) on X-axis and imaginary part of GOL(s) on Y-axis as
Nyquist Stability Criteria:
A feedback control system will be unstable if the Nyquist plot of G(j) encircles point (-1,0) as
The number of encirclements correspond to the number of roots of the characteristic equation that lie in R.H.P. of s –plane assuming that the process is open loop stable.

## Slide 53: BLT Method
A measure of distance of GOL(j) contour from (-1,0) is given as
Suggested design specification for Log Modulus:
Log Modulus Design:
Iteratively choose PI controller parameters such that the design specification is met.
Multivariable Process :
Characteristic Eqn. :

## Slide 54: BLT Method
Define
Encirclement of (-1,0) by f(j) would indicate instability.
Define a multivariable closed loop log modulus as
Suggested design specification for Log Modulus: for n-dimension system
Tuning Procedure
Calculate Ziegler -Nichol's tuning for n individual PI controllers
Assume a factor F such that 2 ≤ F ≤ 5
De - tune PI controllers as follows:
for j=1,2,.. N
Iteratively choose F such that criteria Lcm = 2n is satisfied.

## Slide 55: BLT: Example

## Slide 56: BLT: Example

## Slide 57: BLT: Example

## Slide 58: Dynamic RGA
Process Model:
Dynamic RGA

## Slide 59: Principles of Decoupling

## Slide 60: Block Diagram : Quad Tank

## Slide 61: Simplified Decoupling
Two compensator Blocks gI1 and gI2
Controller output v1 and v2
Actual control on the process u1 and u2
Without compensator
u1 = v1 and u2=v2
Process model :
With Compensator
Loop 2 informed of changes
of v1 by gI2 and u2 is adjusted
Same for Loop 1

## Slide 62: Simplified Decoupler Design
Process Model
u-v relation:
So,
Or,

## Slide 63: Simplified Decoupler Design
Ideally, should be affected by only and should be affected by only. This means,
So,
and

## Slide 64: Simplified Decoupler Design
Decoupler Equation
Steady State Decoupler

## Slide 65: Quad tank : Decoupler Design
Steady State Decoupler :

## Slide 66: Quad tank : Decoupler Design
Full Decoupler :

## Slide 67: Example: Wood Berry Distillation Column

## Slide 68: Difficulties in simplied Decoupler design

## Slide 69: Generalized Decoupler Design

## Slide 70: Example: Wood Berry Distillation Column

## Slide 71: Steady State Decoupler Design

## Slide 72: Example: Wood Berry Distillation Column

## Slide 73: Simplified Vs Generalized Decoupler

## Slide 74: Challenges in Decoupler Design

## Slide 75: Challenges in Decoupler Design

## Slide 76: Example Problem

## Slide 77: Example Problem
Alternate Solution

## Slide 78: Partial Decoupling

## Slide 79: Partial Decoupling Example